## Mapping Table
Parameter | TIPOLOGIA | NOTE | Unit | Details | Resolution | Data Type | Access | Register (Hex) | Nr of quantities | Size | Nr of registers | Functionality group
Active energy - import | ENERGIA | energia totale | kWh |  | 0.01 | Unsigned | Read | 5000 | 1 | 4 | 4 | Data Reading - Energy (total)
Active energy - export |  |  | kWh |  | 0.01 | Unsigned | Read | 5004 | 1 | 4 | 4 | Data Reading - Energy (total)
Active energy - net |  |  | kWh |  | 0.01 | Signed | Read | 5008 | 1 | 4 | 4 | Data Reading - Energy (total)
Reactive energy - import |  | energia totale | kvarh |  | 0.01 | Unsigned | Read | 500C | 1 | 4 | 4 | Data Reading - Energy (total)
Reactive energy - export |  |  | kvarh |  | 0.01 | Unsigned | Read | 5010 | 1 | 4 | 4 | Data Reading - Energy (total)
Reactive energy - net |  |  | kvarh |  | 0.01 | Signed | Read | 5014 | 1 | 4 | 4 | Data Reading - Energy (total)
Apparent energy - import |  | energia totale | kVA |  | 0.01 | Unsigned | Read | 5018 | 1 | 4 | 4 | Data Reading - Energy (total)
Apparent energy - export |  |  | kVA |  | 0.01 | Unsigned | Read | 501C | 1 | 4 | 4 | Data Reading - Energy (total)
Apparent energy - net |  |  | kVA |  | 0.01 | Signed | Read | 5020 | 1 | 4 | 4 | Data Reading - Energy (total)
Active energy - import |  | Conversione | kg / kWh | CO2 conversion factor | 0.001 | Unsigned | Read | 5024 | 1 | 4 | 4 | Data Reading - Energy Conversion
Active energy - import |  | Conversione | Currency / kWh | Currency conversion factor | 0.001 | Unsigned | Read | 5034 | 1 | 4 | 4 | Data Reading - Energy Conversion
Active energy - import |  |  | kWh | L1, L2, L3 | 0.01 | Unsigned | Read | 5460 | 3 | 4 | 12 | Data Reading - Energy (per phase)
Active energy - export |  |  | kWh | L1, L2, L3 | 0.01 | Unsigned | Read | 546C | 3 | 4 | 12 | Data Reading - Energy (per phase)
Active energy - net |  |  | kWh | L1, L2, L3 | 0.01 | Signed | Read | 5478 | 3 | 4 | 12 | Data Reading - Energy (per phase)
Reactive energy - import |  |  | kvarh | L1, L2, L3 | 0.01 | Unsigned | Read | 5484 | 3 | 4 | 12 | Data Reading - Energy (per phase)
Reactive energy - export |  |  | kvarh | L1, L2, L3 | 0.01 | Unsigned | Read | 5490 | 3 | 4 | 12 | Data Reading - Energy (per phase)
Reactive energy - net |  |  | kvarh | L1, L2, L3 | 0.01 | Signed | Read | 549C | 3 | 4 | 12 | Data Reading - Energy (per phase)
Apparent energy - import |  |  | kVA | L1, L2, L3 | 0.01 | Unsigned | Read | 54A8 | 3 | 4 | 12 | Data Reading - Energy (per phase)
Apparent energy - export |  |  | kVA | L1, L2, L3 | 0.01 | Unsigned | Read | 54B4 | 3 | 4 | 12 | Data Reading - Energy (per phase)
Apparent energy - net |  |  | kVA | L1, L2, L3 | 0.01 | Signed | Read | 54C0 | 3 | 4 | 12 | Data Reading - Energy (per phase)
Three phase system voltage | TENSIONE |  | V |  | 0.1 | Unsigned | Read | 5B00 | 1 | 2 | 2 | Data Reading - Real-Time values
Phase voltage L1 |  |  | V | L1 | 0.1 | Unsigned | Read | 5B02 | 1 | 2 | 2 | Data Reading - Real-Time values
Phase voltage L2 |  |  | V | L2 | 0.1 | Unsigned | Read | 5B04 | 1 | 2 | 2 | Data Reading - Real-Time values
Phase voltage L3 |  |  | V | L3 | 0.1 | Unsigned | Read | 5B06 | 1 | 2 | 2 | Data Reading - Real-Time values
Line voltage L1-L2 |  |  | V | L1-L2 | 0.1 | Unsigned | Read | 5B08 | 1 | 2 | 2 | Data Reading - Real-Time values
Line voltage L3-L2 |  |  | V | L3-L2 | 0.1 | Unsigned | Read | 5B0A | 1 | 2 | 2 | Data Reading - Real-Time values
Line voltage L1-L3 |  |  | V | L1-L3 | 0.1 | Unsigned | Read | 5B0C | 1 | 2 | 2 | Data Reading - Real-Time values
Three phase system current | CORRENTE |  | A |  | 0.01 | Unsigned | Read | 5B0E | 1 | 2 | 2 | Data Reading - Real-Time values
Current |  |  | A | L1 | 0.01 | Unsigned | Read | 5B10 | 1 | 2 | 2 | Data Reading - Real-Time values
Current |  |  | A | L2 | 0.01 | Unsigned | Read | 5B12 | 1 | 2 | 2 | Data Reading - Real-Time values
Current |  |  | A | L3 | 0.01 | Unsigned | Read | 5B14 | 1 | 2 | 2 | Data Reading - Real-Time values
Current |  |  | A | N | 0.01 | Unsigned | Read | 5B16 | 1 | 2 | 2 | Data Reading - Real-Time values
Active power | POTENZA |  | W | Total | 0.01 | Signed | Read | 5B1A | 1 | 2 | 2 | Data Reading - Real-Time values
Active power |  |  | W | L1 | 0.01 | Signed | Read | 5B1C | 1 | 2 | 2 | Data Reading - Real-Time values
Active power |  |  | W | L2 | 0.01 | Signed | Read | 5B1E | 1 | 2 | 2 | Data Reading - Real-Time values
Active power |  |  | W | L3 | 0.01 | Signed | Read | 5B20 | 1 | 2 | 2 | Data Reading - Real-Time values
Reactive power |  |  | var | Total | 0.01 | Signed | Read | 5B22 | 1 | 2 | 2 | Data Reading - Real-Time values
Reactive power |  |  | var | L1 | 0.01 | Signed | Read | 5B24 | 1 | 2 | 2 | Data Reading - Real-Time values
Reactive power |  |  | var | L2 | 0.01 | Signed | Read | 5B26 | 1 | 2 | 2 | Data Reading - Real-Time values
Reactive power |  |  | var | L3 | 0.01 | Signed | Read | 5B28 | 1 | 2 | 2 | Data Reading - Real-Time values
Apparent power |  |  | VA | Total | 0.01 | Signed | Read | 5B2A | 1 | 2 | 2 | Data Reading - Real-Time values
Apparent power |  |  | VA | L1 | 0.01 | Signed | Read | 5B2C | 1 | 2 | 2 | Data Reading - Real-Time values
Apparent power |  |  | VA | L2 | 0.01 | Signed | Read | 5B2E | 1 | 2 | 2 | Data Reading - Real-Time values
Apparent power |  |  | VA | L3 | 0.01 | Signed | Read | 5B30 | 1 | 2 | 2 | Data Reading - Real-Time values
Frequency | FREQUENZA |  | Hz |  | 0.01 | Unsigned | Read | 5B32 | 1 | 1 | 1 | Data Reading - Real-Time values
Phase angles power | FATTORI POTENZA |  | ° | Total, L1, L2, L3 | 0.1 | Signed | Read | 5B33 | 4 | 1 | 4 | Data Reading - Real-Time values
Phase angles voltage |  |  | ° | L1, L2, L3 | 0.1 | Signed | Read | 5B37 | 3 | 1 | 3 | Data Reading - Real-Time values
Phase angles current |  |  | ° | L1, L2, L3 | 0.1 | Signed | Read | 5B3D | 3 | 1 | 3 | Data Reading - Real-Time values
Power factors |  |  |  | Total | 0.001 | Signed | Read | 5B40 | 1 | 1 | 1 | Data Reading - Real-Time values
Power factors |  |  |  | L1 | 0.001 | Signed | Read | 5B41 | 1 | 1 | 1 | Data Reading - Real-Time values
Power factors |  |  |  | L2 | 0.001 | Signed | Read | 5B42 | 1 | 1 | 1 | Data Reading - Real-Time values
Power factors |  |  |  | L3 | 0.001 | Signed | Read | 5B43 | 1 | 1 | 1 | Data Reading - Real-Time values
Current quadrant |  |  |  | Total, L1, L2, L3 | 1 | Unsigned | Read | 5B44 | 4 | 1 | 4 | Data Reading - Real-Time values
Cosphi (displacement factor) |  |  | ° | Total | 0.001 | Signed | Read | 5B48 | 1 | 1 | 1 | Data Reading - Real-Time values
Cosphi (displacement factor) |  |  | ° | L1 | 0.001 | Signed | Read | 5B49 | 1 | 1 | 1 | Data Reading - Real-Time values
Cosphi (displacement factor) |  |  | ° | L2 | 0.001 | Signed | Read | 5B4A | 1 | 1 | 1 | Data Reading - Real-Time values
Cosphi (displacement factor) |  |  | ° | L3 | 0.001 | Signed | Read | 5B4B | 1 | 1 | 1 | Data Reading - Real-Time values
Average current L1 | VALORI MEDI |  | A | Data value | 0.01 | Unsigned | Read | 5BD4 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average current L2 |  |  | A | Data value | 0.01 | Unsigned | Read | 5BD6 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average current L3 |  |  | A | Data value | 0.01 | Unsigned | Read | 5BD8 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average current neutral |  |  | A | Data value | 0.01 | Unsigned | Read | 5BDA | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average voltage L1 |  |  | V | Data value | 0.1 | Unsigned | Read | 5BDC | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average voltage L2 |  |  | V | Data value | 0.1 | Unsigned | Read | 5BDE | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average voltage L3 |  |  | V | Data value | 0.1 | Unsigned | Read | 5BE0 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average voltage L1-L2 |  |  | V | Data value | 0.1 | Unsigned | Read | 5BE2 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average voltage L2-L3 |  |  | V | Data value | 0.1 | Unsigned | Read | 5BE4 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average voltage L1-L3 |  |  | V | Data value | 0.1 | Unsigned | Read | 5BE6 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average active power total |  |  | W | Data value | 0.01 | Signed | Read | 5BE8 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average active power L1 |  |  | W | Data value | 0.01 | Signed | Read | 5BEA | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average active power L2 |  |  | W | Data value | 0.01 | Signed | Read | 5BEC | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average active power L3 |  |  | W | Data value | 0.01 | Signed | Read | 5BEE | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average reactive power total |  |  | var | Data value | 0.01 | Signed | Read | 5BF0 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average reactive power L1 |  |  | var | Data value | 0.01 | Signed | Read | 5BF2 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average reactive power L2 |  |  | var | Data value | 0.01 | Signed | Read | 5BF4 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average reactive power L3 |  |  | var | Data value | 0.01 | Signed | Read | 5BF6 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average apparent power total |  |  | VA | Data value | 0.01 | Signed | Read | 5BF8 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average apparent power L1 |  |  | VA | Data value | 0.01 | Signed | Read | 5BFA | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average apparent power L2 |  |  | VA | Data value | 0.01 | Signed | Read | 5BFC | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average apparent power L3 |  |  | VA | Data value | 0.01 | Signed | Read | 5BFE | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum current L1 | VALORI MASSIMI |  | A | Data value | 0.01 | Unsigned | Read | 5C10 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum current L2 |  |  | A | Data value | 0.01 | Unsigned | Read | 5C12 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum current L3 |  |  | A | Data value | 0.01 | Unsigned | Read | 5C14 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum current neutral |  |  | A | Data value | 0.01 | Unsigned | Read | 5C16 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum voltage L1 |  |  | V | Data value | 0.1 | Unsigned | Read | 5C18 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum voltage L2 |  |  | V | Data value | 0.1 | Unsigned | Read | 5C1A | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum voltage L3 |  |  | V | Data value | 0.1 | Unsigned | Read | 5C1C | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum voltage L1-L2 |  |  | V | Data value | 0.1 | Unsigned | Read | 5C1E | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum voltage L2-L3 |  |  | V | Data value | 0.1 | Unsigned | Read | 5C20 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum voltage L1-L3 |  |  | V | Data value | 0.1 | Unsigned | Read | 5C22 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum active power total |  |  | W | Data value | 0.01 | Signed | Read | 5C24 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum active power L1 |  |  | W | Data value | 0.01 | Signed | Read | 5C26 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum active power L2 |  |  | W | Data value | 0.01 | Signed | Read | 5C28 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum active power L3 |  |  | W | Data value | 0.01 | Signed | Read | 5C2A | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum reactive power total |  |  | var | Data value | 0.01 | Signed | Read | 5C2C | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum reactive power L1 |  |  | var | Data value | 0.01 | Signed | Read | 5C2E | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum reactive power L2 |  |  | var | Data value | 0.01 | Signed | Read | 5C30 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum reactive power L3 |  |  | var | Data value | 0.01 | Signed | Read | 5C32 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum apparent power total |  |  | VA | Data value | 0.01 | Signed | Read | 5C34 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum apparent power L1 |  |  | VA | Data value | 0.01 | Signed | Read | 5C36 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum apparent power L2 |  |  | VA | Data value | 0.01 | Signed | Read | 5C38 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum apparent power L3 |  |  | VA | Data value | 0.01 | Signed | Read | 5C3A | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum current L1 timestamp | TIMESTAMP VALORI MASSIMI |  |  | Timestamp |  | Unsigned | Read | 5C4C | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum current L2 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C4E | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum current L3 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C50 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum current neutral timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C52 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum voltage L1 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C54 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum voltage L2 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C56 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum voltage L3 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C58 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum voltage L1-L2 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C5A | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum voltage L2-L3 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C5C | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum voltage L1-L3 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C5E | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum active power total timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C60 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum active power L1 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C62 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum active power L2 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C64 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum active power L3 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C66 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum reactive power total timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C68 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum reactive power L1 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C6A | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum reactive power L2 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C6C | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum reactive power L3 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C6E | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum apparent power total timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C70 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum apparent power L1 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C72 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum apparent power L2 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C74 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Maximum apparent power L3 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5C76 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum current L1 | VALORI MINIMI |  | A | Data value | 0.01 | Unsigned | Read | 5C88 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum current L2 |  |  | A | Data value | 0.01 | Unsigned | Read | 5C8A | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum current L3 |  |  | A | Data value | 0.01 | Unsigned | Read | 5C8C | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum current neutral |  |  | A | Data value | 0.01 | Unsigned | Read | 5C8E | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum voltage L1 |  |  | V | Data value | 0.1 | Unsigned | Read | 5C90 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum voltage L2 |  |  | V | Data value | 0.1 | Unsigned | Read | 5C92 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum voltage L3 |  |  | V | Data value | 0.1 | Unsigned | Read | 5C94 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum voltage L1-L2 |  |  | V | Data value | 0.1 | Unsigned | Read | 5C96 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum voltage L2-L3 |  |  | V | Data value | 0.1 | Unsigned | Read | 5C98 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum voltage L1-L3 |  |  | V | Data value | 0.1 | Unsigned | Read | 5C9A | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum active power total |  |  | W | Data value | 0.01 | Signed | Read | 5C9C | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum active power L1 |  |  | W | Data value | 0.01 | Signed | Read | 5C9E | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum active power L2 |  |  | W | Data value | 0.01 | Signed | Read | 5CA0 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum active power L3 |  |  | W | Data value | 0.01 | Signed | Read | 5CA2 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum reactive power total |  |  | var | Data value | 0.01 | Signed | Read | 5CA4 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum reactive power L1 |  |  | var | Data value | 0.01 | Signed | Read | 5CA6 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum reactive power L2 |  |  | var | Data value | 0.01 | Signed | Read | 5CA8 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum reactive power L3 |  |  | var | Data value | 0.01 | Signed | Read | 5CAA | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum apparent power total |  |  | VA | Data value | 0.01 | Signed | Read | 5CAC | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum apparent power L1 |  |  | VA | Data value | 0.01 | Signed | Read | 5CAE | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum apparent power L2 |  |  | VA | Data value | 0.01 | Signed | Read | 5CB0 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum apparent power L3 |  |  | VA | Data value | 0.01 | Signed | Read | 5CB2 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum current L1 timestamp | TIMESTAMP VALORI MINIMI |  |  | Timestamp |  | Unsigned | Read | 5CC4 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum current L2 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CC6 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum current L3 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CC8 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum current neutral timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CCA | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum voltage L1 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CCC | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum voltage L2 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CCE | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum voltage L3 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CD0 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum voltage L1-L2 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CD2 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum voltage L2-L3 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CD4 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum voltage L1-L3 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CD6 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum active power total timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CD8 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum active power L1 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CDA | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum active power L2 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CDC | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum active power L3 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CDE | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum reactive power total timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CE0 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum reactive power L1 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CE2 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum reactive power L2 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CE4 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum reactive power L3 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CE6 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum apparent power total timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CE8 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum apparent power L1 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CEA | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum apparent power L2 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CEC | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Minimum apparent power L3 timestamp |  |  |  | Timestamp |  | Unsigned | Read | 5CEE | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Voltage THD harmonics | THD TENSIONE |  | % | L1 (THD) | 0.1 | Unsigned | Read | 5D00 | 1 | 1 | 1 | Data Reading - Power Quality
|  | fatto 2nd-7th |  | L1 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 5D01 | 39 | 1 | 39 | Data Reading - Power Quality
|  |  | % | L2 (THD) | 0.1 | Unsigned | Read | 5D80 | 1 | 1 | 1 | Data Reading - Power Quality
|  | fatto 2nd-7th |  | L2 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 5D81 | 39 | 1 | 39 | Data Reading - Power Quality
|  |  | % | L3 (THD) | 0.1 | Unsigned | Read | 5E00 | 1 | 1 | 1 | Data Reading - Power Quality
|  | fatto 2nd-7th |  | L3 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 5E01 | 39 | 1 | 39 | Data Reading - Power Quality
|  |  | % | L1-L2 (THD) | 0.1 | Unsigned | Read | 5E80 | 1 | 1 | 1 | Data Reading - Power Quality
|  | fatto 2nd-7th |  | L1-L2 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 5E81 | 39 | 1 | 39 | Data Reading - Power Quality
|  |  | % | L3-L2 (THD) | 0.1 | Unsigned | Read | 5F00 | 1 | 1 | 1 | Data Reading - Power Quality
|  | fatto 2nd-7th |  | L3-L2 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 5F01 | 39 | 1 | 39 | Data Reading - Power Quality
|  |  | % | L1-L3 (THD) | 0.1 | Unsigned | Read | 5F80 | 1 | 1 | 1 | Data Reading - Power Quality
|  | fatto 2nd-7th |  | L1-L3 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 5F81 | 39 | 1 | 39 | Data Reading - Power Quality
Current harmonics | THD CORRENTE |  | % | L1 (THD) | 0.1 | Unsigned | Read | 6000 | 1 | 1 | 1 | Data Reading - Power Quality
|  | fatto 2nd-7th |  | L1 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 6001 | 39 | 1 | 39 | Data Reading - Power Quality
|  |  | % | L2 (THD) | 0.1 | Unsigned | Read | 6080 | 1 | 1 | 1 | Data Reading - Power Quality
|  | fatto 2nd-7th |  | L2 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 6081 | 39 | 1 | 39 | Data Reading - Power Quality
|  |  | % | L3 (THD) | 0.1 | Unsigned | Read | 6100 | 1 | 1 | 1 | Data Reading - Power Quality
|  | fatto 2nd-7th |  | L3 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 6101 | 39 | 1 | 39 | Data Reading - Power Quality
|  |  | % | N (THD) | 0.1 | Unsigned | Read | 6180 | 1 | 1 | 1 | Data Reading - Power Quality
|  | fatto 2nd-7th |  | N (2nd,3rd…40th) | 0.1 | Unsigned | Read | 6181 | 39 | 1 | 39 | Data Reading - Power Quality
Unbalances | SBILANCI |  | % | Line voltage | 0.1 | Unsigned | Read | 6200 | 1 | 2 | 2 | Data Reading - Power Quality
|  |  | % | Phase voltage | 0.1 | Unsigned | Read | 6202 | 1 | 2 | 2 | Data Reading - Power Quality
|  |  | % | Current | 0.1 | Unsigned | Read | 6204 | 1 | 2 | 2 | Data Reading - Power Quality
Outputs |  |  | 0: OFF, 1: ON | Output 1 |  |  | Read/Write | 6300 | 1 | 1 | 1 | Data Reading - I/O
|  |  | 0: OFF, 1: ON | Output 2 |  |  | Read/Write | 6301 | 1 | 1 | 1 | Data Reading - I/O
Errors Log |  |  |  | Header - Get next entry |  | Unsigned | Write | 6500 | 1 | 1 | 1 | Data Reading - Notifications
|  |  |  | Header - Entry Number |  | Unsigned | Read/Write | 6501 | 1 | 1 | 1 | Data Reading - Notifications
|  |  |  | Header - Direction |  | Unsigned | Read/Write | 6507 | 1 | 1 | 1 | Data Reading - Notifications
|  |  |  | Data block |  |  | Read | 6510 | 1 | 105 | 105 | Data Reading - Notifications
Alarms log |  |  |  | Header - Get next entry |  | Unsigned | Write | 65B0 | 1 | 1 | 1 | Data Reading - Notifications
|  |  |  | Header - Entry Number |  | Unsigned | Read/Write | 65B1 | 1 | 1 | 1 | Data Reading - Notifications
|  |  |  | Header - Direction |  | Unsigned | Read/Write | 65B7 | 1 | 1 | 1 | Data Reading - Notifications
|  |  |  | Data block |  |  | Read | 65C0 | 1 | 105 | 105 | Data Reading - Notifications
Audit Log |  |  |  | Header - Get next entry |  | Unsigned | Write | 6660 | 1 | 1 | 1 | Data Reading - Notifications
|  |  |  | Header - Entry Number |  | Unsigned | Read/Write | 6661 | 1 | 1 | 1 | Data Reading - Notifications
|  |  |  | Header - Direction |  | Unsigned | Read/Write | 6667 | 1 | 1 | 1 | Data Reading - Notifications
|  |  |  | Data block - Entry_Num |  | Unsigned | Read | 6670 | 1 | 2 | 2 | Data Reading - Notifications
|  |  |  | Data block - Timestamp (seconds from 2010-01-01 |  | Unsigned | Read | 6672 | 1 | 2 | 2 | Data Reading - Notifications
|  |  |  | Data block - Upgrade_Counter |  | Unsigned | Read | 6674 | 1 | 1 | 1 | Data Reading - Notifications
|  |  |  | Data block - FW_Version |  | ASCII | Read | 6675 | 1 | 6 | 6 | Data Reading - Notifications
|  |  |  | Data block - TRAFO_V_Prim |  | Unsigned | Read | 667B | 1 | 2 | 2 | Data Reading - Notifications
|  |  |  | Data block - TRAFO_V_Sec |  | Unsigned | Read | 667D | 1 | 2 | 2 | Data Reading - Notifications
|  |  |  | Data block - TRAFO_I_Prim |  | Unsigned | Read | 667F | 1 | 2 | 2 | Data Reading - Notifications
|  |  |  | Data block - TRAFO_I_Sec |  | Unsigned | Read | 6681 | 1 | 2 | 2 | Data Reading - Notifications
|  |  |  | Data block - TRAFO_IN_Prim |  | Unsigned | Read | 6683 | 1 | 2 | 2 | Data Reading - Notifications
|  |  |  | Data block - TRAFO_IN_Sec |  | Unsigned | Read | 6685 | 1 | 2 | 2 | Data Reading - Notifications
|  |  |  | Data block - WIRES |  | Unsigned | Read | 6687 | 1 | 1 | 1 | Data Reading - Notifications
|  |  |  | Data block - ACTIVE_ENERGY_IMPORT_TOTAL | 0.001 | Unsigned | Read | 6688 | 1 | 4 | 4 | Data Reading - Notifications
|  |  |  | Data block - ACTIVE_ENERGY_IMPORT_L1 | 0.001 | Unsigned | Read | 668C | 1 | 4 | 4 | Data Reading - Notifications
|  |  |  | Data block - ACTIVE_ENERGY_IMPORT_L2 | 0.001 | Unsigned | Read | 6690 | 1 | 4 | 4 | Data Reading - Notifications
|  |  |  | Data block - ACTIVE_ENERGY_IMPORT_L3 | 0.001 | Unsigned | Read | 6694 | 1 | 4 | 4 | Data Reading - Notifications
|  |  |  | Data block - ACTIVE_ENERGY_IMPORT_TAR1 | 0.001 | Unsigned | Read | 6698 | 1 | 4 | 4 | Data Reading - Notifications
|  |  |  | Data block - ACTIVE_ENERGY_IMPORT_TAR2 | 0.001 | Unsigned | Read | 669C | 1 | 4 | 4 | Data Reading - Notifications
|  |  |  | Data block - ACTIVE_ENERGY_IMPORT_TAR3 | 0.001 | Unsigned | Read | 66A0 | 1 | 4 | 4 | Data Reading - Notifications
|  |  |  | Data block - ACTIVE_ENERGY_IMPORT_TAR4 | 0.001 | Unsigned | Read | 66A4 | 1 | 4 | 4 | Data Reading - Notifications
|  |  |  | Data block - ACTIVE_ENERGY_IMPORT_TAR5 | 0.001 | Unsigned | Read | 66A8 | 1 | 4 | 4 | Data Reading - Notifications
|  |  |  | Data block - ACTIVE_ENERGY_IMPORT_TAR6 | 0.001 | Unsigned | Read | 66AC | 1 | 4 | 4 | Data Reading - Notifications
|  |  |  | Data block - ACTIVE_ENERGY_EXPORT_TOTAL | 0.001 | Unsigned | Read | 66B0 | 1 | 4 | 4 | Data Reading - Notifications
Warnings log |  |  |  | Header - Get next entry |  | Unsigned | Write | 6710 | 1 | 1 | 1 | Data Reading - Notifications
|  |  |  | Header - Entry Number |  | Unsigned | Read/Write | 6711 | 1 | 1 | 1 | Data Reading - Notifications
|  |  |  | Header - Direction |  | Unsigned | Read/Write | 6717 | 1 | 1 | 1 | Data Reading - Notifications
|  |  |  | Data block |  |  | Read | 6720 | 1 | 105 | 105 | Data Reading - Notifications
Power Outage Log |  |  |  | Header - Get next entry |  | Unsigned | Write | 67C0 | 1 | 1 | 1 | Data Reading - Notifications
|  |  |  | Header - Entry Number |  | Unsigned | Read/Write | 67C1 | 1 | 1 | 1 | Data Reading - Notifications
|  |  |  | Header - Direction |  | Unsigned | Read/Write | 67C7 | 1 | 1 | 1 | Data Reading - Notifications
|  |  |  | Data block |  |  | Read | 67D0 | 1 | 105 | 105 | Data Reading - Notifications
Energy Cumulative |  |  |  | Header - Get next entry |  |  | Read/Write | 8000 |  | 1 | 1 | Data Reading - Historicals
|  |  |  | Header - Entry Number |  |  | Read/Write | 8001 |  | 1 | 1 | Data Reading - Historicals
|  |  |  | Header - Date Time |  |  | Read/Write | 8004 |  | 3 | 3 | Data Reading - Historicals
|  |  |  | Header - Direction |  |  | Read/Write | 8007 |  | 1 | 1 | Data Reading - Historicals
|  |  |  | Data block 1 |  |  | Read | 8010 |  | 83 | 83 | Data Reading - Historicals
|  |  |  | Data block 2 |  |  | Read | 8070 |  | 83 | 83 | Data Reading - Historicals
|  |  |  | Data block 3 |  |  | Read | 80D0 |  | 83 | 83 | Data Reading - Historicals
|  |  |  | Data block 4 |  |  | Read | 8130 |  | 83 | 83 | Data Reading - Historicals
|  |  |  | Data block 5 |  |  | Read | 8190 |  | 83 | 83 | Data Reading - Historicals
|  |  |  | Data block 6 |  |  | Read | 81F0 |  | 83 | 83 | Data Reading - Historicals
|  |  |  | Data block 7 |  |  | Read | 8250 |  | 83 | 83 | Data Reading - Historicals
Energy Snapshots |  |  |  | Header - Get next entry |  |  | Read/Write | 8300 |  | 1 | 1 | Data Reading - Historicals
|  |  |  | Header - Entry Number |  |  | Read/Write | 8301 |  | 1 | 1 | Data Reading - Historicals
|  |  |  | Header - Date Time |  |  | Read/Write | 8304 |  | 3 | 3 | Data Reading - Historicals
|  |  |  | Header - Direction |  |  | Read/Write | 8307 |  | 1 | 1 | Data Reading - Historicals
|  |  |  | Data block 1 |  |  | Read | 8310 |  | 83 | 83 | Data Reading - Historicals
|  |  |  | Data block 2 |  |  | Read | 8370 |  | 83 | 83 | Data Reading - Historicals
|  |  |  | Data block 3 |  |  | Read | 83D0 |  | 83 | 83 | Data Reading - Historicals
|  |  |  | Data block 4 |  |  | Read | 8430 |  | 83 | 83 | Data Reading - Historicals
|  |  |  | Data block 5 |  |  | Read | 8490 |  | 83 | 83 | Data Reading - Historicals
|  |  |  | Data block 6 |  |  | Read | 84F0 |  | 83 | 83 | Data Reading - Historicals
|  |  |  | Data block 7 |  |  | Read | 8550 |  | 83 | 83 | Data Reading - Historicals
Load profile |  |  |  | Header - Get next block |  |  | Read/Write | 8700 |  | 1 | 1 | Data Reading - Historicals
|  |  |  | Header - Channel number |  |  | Read/Write | 8703 |  | 1 | 1 | Data Reading - Historicals
|  |  |  | Header - Date / Time |  |  | Read/Write | 8704 |  | 3 | 3 | Data Reading - Historicals
|  |  |  | Header - Direction |  |  | Read/Write | 8707 |  | 1 | 1 | Data Reading - Historicals
|  |  |  | Channel information - quantity |  |  | Read/Write | 8710 |  | 3 | 3 | Data Reading - Historicals
|  |  |  | Channel information - scaler |  |  | Read/Write | 8713 |  | 1 | 1 | Data Reading - Historicals
|  |  |  | Channel information - interval |  |  | Read/Write | 8714 |  | 2 | 2 | Data Reading - Historicals
|  |  |  | Channel information - datatype |  |  | Read/Write | 8716 |  | 1 | 1 | Data Reading - Historicals
|  |  |  | Data block |  |  | Read | 8720 |  | 120 | 120 | Data Reading - Historicals
Serial number(s) | [5 empty] | ASCII | Read | 8900 | 1 | 5 | 5 | Configuration - Device info
Meter firmware version | [5 empty] | ASCII | Read | 8908 | 1 | 8 | 8 | Configuration - Device info
Product type number ID |  |  |  | See Details sheet |  |  | Read | 8910 | 1 | 1 | 1 | Configuration - Device info
Slave ID | [6 empty] | Read | 8911 | 1 | 8 | 8 | Configuration - Device info
Product tag name | [5 empty] | ASCII | Read/Write | 8919 | 1 | 5 | 5 | Configuration - Device info
Type designation |  |  |  | E.g. M4M30SMA |  | ASCII | Read | 8960 | 1 | 6 | 6 | Configuration - Device info
Product Name |  |  |  | E.g. M4M 30 MODBUS |  | ASCII | Read | 8966 | 1 | 8 | 8 | Configuration - Device info
Date Time |  |  |  | YYMMDD:HHMMSS |  |  | Read/Write | 8A00 | 1 | 3 | 3 | Configuration - Date and Time
Error flags |  |  |  | 64 bits flags |  |  | Read only | 8A13 | 1 | 4 | 4 | Data Reading - Notifications
Information flags |  |  | 25 Alarm flags | 64 bits flags |  |  | Read only | 8A19 | 1 | 4 | 4 | Data Reading - Notifications
Warning flags |  |  |  | 64 bits flags |  |  | Read only | 8A1F | 1 | 4 | 4 | Data Reading - Notifications
Alarm flags (simple and complex) |  |  |  | 64 bits flags (25 Alarm flags used) |  |  | Read only | 8A25 | 1 | 4 | 4 | Data Reading - Alarms
Transformer ratios |  |  |  | CT L1,L2,L3 ratio (Numerator) |  | Unsigned | Read/Write | 8C00 | 1 | 2 | 2 | Configuration - Installation
|  |  |  | CT L1,L2,L3 ratio (Denominator) |  | Unsigned | Read/Write | 8C02 | 1 | 2 | 2 | Configuration - Installation
|  |  |  | VT ratio (Numerator) |  | Unsigned | Read/Write | 8C04 | 1 | 2 | 2 | Configuration - Installation
|  |  |  | VT ratio (Denominator) |  | Unsigned | Read/Write | 8C06 | 1 | 2 | 2 | Configuration - Installation
|  |  |  | CT Neutral ratio (Numerator) |  | Unsigned | Read/Write | 8C08 | 1 | 2 | 2 | Configuration - Installation
|  |  |  | CT Neutral ratio (Denominator) |  | Unsigned | Read/Write | 8C0A | 1 | 2 | 2 | Configuration - Installation
I/O settings - Function |  |  |  | I/O port 1 |  |  | Read/Write | 8C0C | 1 | 1 | 1 | Configuration - I/O
|  |  |  | I/O port 2 |  |  | Read/Write | 8C0D | 1 | 1 | 1 | Configuration - I/O
I/O settings - Pulse input/output instance |  |  |  | Pulse input/output instance |  |  | Read/Write | 8C12 | 1 | 1 | 1 | Configuration - I/O
I/O settings - Pulse outputs configuration |  |  |  | Port number |  |  | Read/Write | 8C13 | 1 | 1 | 1 | Configuration - I/O
|  |  | OBIS code | Energy parameter |  |  | Read/Write | 8C14 | 1 | 3 | 3 | Configuration - I/O
|  |  | kWh | Pulse frequency active energy |  |  | Read/Write | 8C17 | 1 | 2 | 2 | Configuration - I/O
|  |  | kvarh | Pulse frequency reactive energy |  |  | Read/Write | 8C19 | 1 | 2 | 2 | Configuration - I/O
|  |  | milliseconds | Pulse length |  |  | Read/Write | 8C1B | 1 | 2 | 2 | Configuration - I/O
|  |  |  | Turn off pulse output |  |  | Read/Write | 8C1D | 1 | 1 | 1 | Configuration - I/O
Load profile settings |  |  |  | Channel number |  |  | Read/Write | 8C20 | 1 | 1 | 1 | Configuration - Historicals
|  |  | OBIS code | Parameter |  |  | Read/Write | 8C21 | 1 | 3 | 3 | Configuration - Historicals
|  |  | minutes | Interval |  |  | Read/Write | 8C24 | 1 | 2 | 2 | Configuration - Historicals
|  |  |  | Max number of snapshot |  |  | Read/Write | 8C26 | 1 | 2 | 2 | Configuration - Historicals
Max/Min Demand settings |  |  |  | Number of quantities |  |  | Read/Write | 8C30 | 1 | 1 | 1 | Configuration - Historicals
|  |  |  | Parameter number |  |  | Read | 8C31 | 1 | 1 | 1 | Configuration - Historicals
|  |  | OBIS code | Parameter |  |  | Read/Write | 8C32 | 1 | 3 | 3 | Configuration - Historicals
|  |  | OBIS code | Level of Min/Max |  |  | Read/Write | 8C35 | 1 | 3 | 3 | Configuration - Historicals
|  |  |  | Number of levels |  |  | Read/Write | 8C38 | 1 | 1 | 1 | Configuration - Historicals
|  |  | minutes | Interval |  |  | Read/Write | 8C39 | 1 | 1 | 1 | Configuration - Historicals
|  |  | minutes | Sub interval |  |  | Read/Write | 8C3A | 1 | 1 | 1 | Configuration - Historicals
|  |  |  | Period |  |  | Read/Write | 8C3B | 1 | 1 | 1 | Configuration - Historicals
Energy Cumulative/Snapshots settings |  |  |  | Number of channel |  |  | Read/Write | 8C50 | 1 | 1 | 1 | Configuration - Historicals
|  |  |  | Channel number |  |  | Read | 8C51 | 1 | 1 | 1 | Configuration - Historicals
|  |  | OBIS code | Quantity |  |  | Read/Write | 8C52 | 1 | 3 | 3 | Configuration - Historicals
|  |  |  | Period |  |  | Read/Write | 8C55 | 1 | 1 | 1 | Configuration - Historicals
Alarm settings |  |  |  | Channel alarm number |  |  | Read/Write | 8C60 | 1 | 1 | 1 | Configuration - Alarms
|  |  | OBIS code | Quantity |  |  | Read/Write | #REF! | 1 | 3 | 3 | Configuration - Alarms
|  |  |  | Threshold |  |  | Read/Write | #REF! | 1 | 4 | 4 | Configuration - Alarms
|  |  | % | Hysteresis |  |  | Read/Write | #REF! | 1 | 1 | 1 | Configuration - Alarms
|  |  | seconds | Delays |  |  | Read/Write | #REF! | 1 | 2 | 2 | Configuration - Alarms
|  |  |  | Type of alarm |  |  | Read/Write | #REF! | 1 | 1 | 1 | Configuration - Alarms
|  |  |  | Action - alarm triggered |  |  | Read/Write | #REF! | 1 | 2 | 2 | Configuration - Alarms
CO2 conversion factor actIive energy |  |  | kg / kWh | Range: 0.001 - 9.999 | 0.001 | Unsigned | Read/Write | 8CE0 | 1 | 2 | 2 | Configuration - Energy Conversion
Currency conversion factor active enenrgy |  |  | Currency / kWh | Range: 0.001 - 999999.000 | 0.001 | Unsigned | Read/Write | 8CE2 | 1 | 2 | 2 | Configuration - Energy Conversion
LED source |  |  |  | 0 = Active energy, 1 = Reactive energy |  |  | Read/Write | 8CE4 | 1 | 1 | 1 | Configuration - I/O
Wires |  |  |  | See Details sheet |  | Unsigned | Read/Write | 8CE5 | 1 | 1 | 1 | Configuration - Installation
Modbus TCP/IP |  |  |  | DHCP: 0-disable; 1- enable |  | Unsigned | Read/Write | 8CEF | 1 | 1 | 1 | Configuration - Communication
|  |  |  | IP: A.B.C.D -> 0xAABBCCDD |  | Unsigned | Read/Write | 8CF0 | 1 | 2 | 2 | Configuration - Communication
|  |  |  | Mask: A.B.C.D -> 0xAABBCCDD |  | Unsigned | Read/Write | 8CF2 | 1 | 2 | 2 | Configuration - Communication
|  |  |  | Gateway: A.B.C.D -> 0xAABBCCDD |  | Unsigned | Read/Write | 8CF4 | 1 | 2 | 2 | Configuration - Communication
|  |  |  | TCP Port: 502(default), 0xFFFF (max value) |  | Unsigned | Read/Write | 8CF6 | 1 | 1 | 1 | Configuration - Communication
Up/Down Counters |  |  |  | Up Counter |  | Unsigned | Read | 8CF7 | 1 | 2 | 2 | Data Reading - Timers
|  |  |  | Down Counter |  | Unsigned | Read | 8CF9 | 1 | 2 | 2 | Data Reading - Timers
|  |  |  | Down Counter Reset Value |  | Unsigned | Read/Write | 8CFB | 1 | 2 | 2 | Configuration - Timers
HMI Config |  |  |  | Brightness (range: 0 - 255) |  | Unsigned | Read/Write | 8CFD | 1 | 1 | 1 | Configuration - Unit
|  |  |  | Language (range: 0-max language number) |  | Unsigned | Read/Write | 8CFE | 1 | 1 | 1 | Configuration - Unit
Bluetooth Enable | [5 empty] | Unsigned | Read/Write | 8EFC | 1 | 1 | 1 | Configuration - Unit
Reset Logs |  |  |  | Write 1 to perform the reset |  | Unsigned | Write | 8F57 | 1 | 1 | 1 | Configuration - Reset
Reset historical functionality |  |  |  | Write 1 to perform the reset |  | Unsigned | Write | 8F58 | 1 | 1 | 1 | Configuration - Reset
Reset Timer |  |  |  | Write 1 to perform the reset |  | Unsigned | Write | 8F59 | 1 | 1 | 1 | Configuration - Reset
Reset Energy |  |  |  | Write 1 to perform the reset |  | Unsigned | Write | 8F5A | 1 | 1 | 1 | Configuration - Reset
Reset Factory setting default |  |  |  | Write 1 to perform the reset |  | Unsigned | Write | 8F5B | 1 | 1 | 1 | Configuration - Reset
Reset Max / Min / Average |  |  |  | Write 1 to perform the reset |  | Unsigned | Write | 8F5C | 1 | 1 | 1 | Configuration - Reset
Max/Min Demand |  |  |  | Header - Get next entry |  |  | Read/Write | 8F72 |  | 1 | 1 | Configuration - Historicals
|  |  |  | Header - Entry number |  |  | Read/Write | 8F73 |  | 1 | 1 | Configuration - Historicals
|  |  |  | Header - Date / time |  |  | Read/Write | 8F76 |  | 3 | 3 | Configuration - Historicals
|  |  |  | Header - Direction |  |  | Read/Write | 8F79 |  | 1 | 1 | Configuration - Historicals
|  |  |  | Data Block 1 |  |  | Read | 8F82 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 2 |  |  | Read | 9002 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 3 |  |  | Read | 9082 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 4 |  |  | Read | 9102 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 5 |  |  | Read | 9182 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 6 |  |  | Read | 9202 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 7 |  |  | Read | 9282 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 8 |  |  | Read | 9302 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 9 |  |  | Read | 9382 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 10 |  |  | Read | 9402 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 11 |  |  | Read | 9482 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 12 |  |  | Read | 9502 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 13 |  |  | Read | 9582 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 14 |  |  | Read | 9602 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 15 |  |  | Read | 9682 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 16 |  |  | Read | 9702 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 17 |  |  | Read | 9782 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 18 |  |  | Read | 9802 |  | 115 | 115 | Configuration - Historicals
|  |  |  | Data Block 19 |  |  | Read | 9882 |  | 115 | 115 | Configuration - Historicals
Active power total Scaler 1 |  |  | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB1A | 1 | 2 | 2 | Data Reading - Real-Time values
Active power L1 Scaler 1 |  |  | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB1C | 1 | 2 | 2 | Data Reading - Real-Time values
Active power L2 Scaler 1 |  |  | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB1E | 1 | 2 | 2 | Data Reading - Real-Time values
Active power L3 Scaler 1 |  |  | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB20 | 1 | 2 | 2 | Data Reading - Real-Time values
Reactive power total Scaler 1 |  |  | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB22 | 1 | 2 | 2 | Data Reading - Real-Time values
Reactive power L1 Scaler 1 |  |  | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB24 | 1 | 2 | 2 | Data Reading - Real-Time values
Reactive power L2 Scaler 1 |  |  | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB26 | 1 | 2 | 2 | Data Reading - Real-Time values
Reactive power L3 Scaler 1 |  |  | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB28 | 1 | 2 | 2 | Data Reading - Real-Time values
Apparent power total Scaler 1 |  |  | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB2A | 1 | 2 | 2 | Data Reading - Real-Time values
Apparent power L1 Scaler 1 |  |  | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB2C | 1 | 2 | 2 | Data Reading - Real-Time values
Apparent power L2 Scaler 1 |  |  | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB2E | 1 | 2 | 2 | Data Reading - Real-Time values
Apparent power L3 Scaler 1 |  |  | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB30 | 1 | 2 | 2 | Data Reading - Real-Time values
Average Active power total Scaler 1 |  |  | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBE8 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average Active power L1 Scaler 1 |  |  | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBEA | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average Active power L2 Scaler 1 |  |  | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBEC | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average Active power L3 Scaler 1 |  |  | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBEE | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average Reactive power total Scaler 1 |  |  | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBF0 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average Reactive power L1 Scaler 1 |  |  | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBF2 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average Reactive power L2 Scaler 1 |  |  | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBF4 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average Reactive power L3 Scaler 1 |  |  | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBF6 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average Apparent power total Scaler 1 |  |  | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBF8 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average Apparent power L1 Scaler 1 |  |  | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBFA | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average Apparent power L2 Scaler 1 |  |  | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBFC | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Average Apparent power L3 Scaler 1 |  |  | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBFE | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Max Active power total Scaler 1 |  |  | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC24 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Max Active power L1 Scaler 1 |  |  | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC26 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Max Active power L2 Scaler 1 |  |  | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC28 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Max Active power L3 Scaler 1 |  |  | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC2A | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Max Reactive power total Scaler 1 |  |  | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC2C | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Max Reactive power L1 Scaler 1 |  |  | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC2E | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Max Reactive power L2 Scaler 1 |  |  | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC30 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Max Reactive power L3 Scaler 1 |  |  | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC32 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Max Apparent power total Scaler 1 |  |  | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC34 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Max Apparent power L1 Scaler 1 |  |  | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC36 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Max Apparent power L2 Scaler 1 |  |  | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC38 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Max Apparent power L3 Scaler 1 |  |  | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC3A | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Min Active power total Scaler 1 |  |  | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC9C | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Min Active power L1 Scaler 1 |  |  | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC9E | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Min Active power L2 Scaler 1 |  |  | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCA0 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Min Active power L3 Scaler 1 |  |  | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCA2 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Min Reactive power total Scaler 1 |  |  | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCA4 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Min Reactive power L1 Scaler 1 |  |  | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCA6 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Min Reactive power L2 Scaler 1 |  |  | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCA8 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Min Reactive power L3 Scaler 1 |  |  | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCAA | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Min Apparent power total Scaler 1 |  |  | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCAC | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Min Apparent power L1 Scaler 1 |  |  | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCAE | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Min Apparent power L2 Scaler 1 |  |  | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCB0 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values
Min Apparent power L3 Scaler 1 |  |  | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCB2 | 1 | 2 | 2 | Data Reading - Avg/Min/Max values

## LEGENDA
Da implementare
Fatte
Inutili
Registri di configurazione
In lavorazione
Simulati Python

## Foglio3
Parameter |  | Unit | Details | Resolution | Data type | Register | Quantities | Size | Nr. of reg.
Active energy | ENERGIA | kWh |  | 0.01 | Unsigned | 5000 | 1 | 4 | 4
Reactive energy |  | kvarh |  | 0.01 | Unsigned | 500C | 1 | 4 | 4
Apparent energy |  | kVA |  | 0.01 | Unsigned | 5018 | 1 | 4 | 4
Active energy |  | kWh | L1, L2, L3 | 0.01 | Unsigned | 5460 | 3 | 4 | 12
Reactive energy |  | kvarh | L1, L2, L3 | 0.01 | Unsigned | 5484 | 3 | 4 | 12
Apparent energy |  | kVA | L1, L2, L3 | 0.01 | Unsigned | 54A8 | 3 | 4 | 12
Three phase system voltage | TENSIONE | V |  | 0.1 | Unsigned | 5B00 | 1 | 2 | 2
Voltage L1-N |  | V |  | 0.1 | Unsigned | 5B02 | 1 | 2 | 2
Voltage L2-N |  | V |  | 0.1 | Unsigned | 5B04 | 1 | 2 | 2
Voltage L3-N |  | V |  | 0.1 | Unsigned | 5B06 | 1 | 2 | 2
Voltage L1-L2 |  | V |  | 0.1 | Unsigned | 5B08 | 1 | 2 | 2
Voltage L3-L2 |  | V |  | 0.1 | Unsigned | 5B0A | 1 | 2 | 2
Voltage L1-L3 |  | V |  | 0.1 | Unsigned | 5B0C | 1 | 2 | 2
Three phase system current | CORRENTE | A |  | 0.01 | Unsigned | 5B0E | 1 | 2 | 2
Current L1 |  | A |  | 0.01 | Unsigned | 5B10 | 1 | 2 | 2
Current L2 |  | A |  | 0.01 | Unsigned | 5B12 | 1 | 2 | 2
Current L3 |  | A |  | 0.01 | Unsigned | 5B14 | 1 | 2 | 2
Current N |  | A |  | 0.01 | Unsigned | 5B16 | 1 | 2 | 2
Active power total | POTENZA | W |  | 0.01 | Signed | 5B1A | 1 | 2 | 2
Active power L1 |  | W |  | 0.01 | Signed | 5B1C | 1 | 2 | 2
Active power L2 |  | W |  | 0.01 | Signed | 5B1E | 1 | 2 | 2
Active power L3 |  | W |  | 0.01 | Signed | 5B20 | 1 | 2 | 2
Reactive power total |  | var |  | 0.01 | Signed | 5B22 | 1 | 2 | 2
Reactive power L1 |  | var |  | 0.01 | Signed | 5B24 | 1 | 2 | 2
Reactive power L2 |  | var |  | 0.01 | Signed | 5B26 | 1 | 2 | 2
Reactive power L3 |  | var |  | 0.01 | Signed | 5B28 | 1 | 2 | 2
Apparent power total |  | VA |  | 0.01 | Signed | 5B2A | 1 | 2 | 2
Apparent power L1 |  | VA |  | 0.01 | Signed | 5B2C | 1 | 2 | 2
Apparent power L2 |  | VA |  | 0.01 | Signed | 5B2E | 1 | 2 | 2
Apparent power L3 |  | VA |  | 0.01 | Signed | 5B30 | 1 | 2 | 2
Frequency | FREQUENZA | Hz |  | 0.01 | Unsigned | 5B32 | 1 | 1 | 1
Phase angles power | FATTORI POTENZA | ° | Total, L1, L2, L3 | 0.1 | Signed | 5B33 | 4 | 1 | 4
Phase angles voltage |  | ° | L1, L2, L3 | 0.1 | Signed | 5B37 | 3 | 1 | 3
Phase angles current |  | ° | L1, L2, L3 | 0.1 | Signed | 5B3D | 3 | 1 | 3
Power factor total |  |  |  | 0.001 | Signed | 5B40 | 1 | 1 | 1
Power factor L1 |  |  |  | 0.001 | Signed | 5B41 | 1 | 1 | 1
Power factor L2 |  |  |  | 0.001 | Signed | 5B42 | 1 | 1 | 1
Power factor L3 |  |  |  | 0.001 | Signed | 5B43 | 1 | 1 | 1
Current quadrant |  |  | Total, L1, L2, L3 | 1 | Unsigned | 5B44 | 4 | 1 | 4
Cosphi total |  | ° |  | 0.001 | Signed | 5B48 | 1 | 1 | 1
Cosphi L1 |  | ° |  | 0.001 | Signed | 5B49 | 1 | 1 | 1
Cosphi L2 |  | ° |  | 0.001 | Signed | 5B4A | 1 | 1 | 1
Cosphi L3 |  | ° |  | 0.001 | Signed | 5B4B | 1 | 1 | 1
Maximum current L1 | VALORI MASSIMI | A | Data value | 0.01 | Unsigned | 5C10 | 1 | 2 | 2
Maximum current L2 |  | A | Data value | 0.01 | Unsigned | 5C12 | 1 | 2 | 2
Maximum current L3 |  | A | Data value | 0.01 | Unsigned | 5C14 | 1 | 2 | 2
Maximum current neutral |  | A | Data value | 0.01 | Unsigned | 5C16 | 1 | 2 | 2
Maximum voltage L1 |  | V | Data value | 0.1 | Unsigned | 5C18 | 1 | 2 | 2
Maximum voltage L2 |  | V | Data value | 0.1 | Unsigned | 5C1A | 1 | 2 | 2
Maximum voltage L3 |  | V | Data value | 0.1 | Unsigned | 5C1C | 1 | 2 | 2
Maximum voltage L1-L2 |  | V | Data value | 0.1 | Unsigned | 5C1E | 1 | 2 | 2
Maximum voltage L2-L3 |  | V | Data value | 0.1 | Unsigned | 5C20 | 1 | 2 | 2
Maximum voltage L1-L3 |  | V | Data value | 0.1 | Unsigned | 5C22 | 1 | 2 | 2
Maximum active power total |  | W | Data value | 0.01 | Signed | 5C24 | 1 | 2 | 2
Maximum active power L1 |  | W | Data value | 0.01 | Signed | 5C26 | 1 | 2 | 2
Maximum active power L2 |  | W | Data value | 0.01 | Signed | 5C28 | 1 | 2 | 2
Maximum active power L3 |  | W | Data value | 0.01 | Signed | 5C2A | 1 | 2 | 2
Maximum reactive power total |  | var | Data value | 0.01 | Signed | 5C2C | 1 | 2 | 2
Maximum reactive power L1 |  | var | Data value | 0.01 | Signed | 5C2E | 1 | 2 | 2
Maximum reactive power L2 |  | var | Data value | 0.01 | Signed | 5C30 | 1 | 2 | 2
Maximum reactive power L3 |  | var | Data value | 0.01 | Signed | 5C32 | 1 | 2 | 2
Maximum apparent power total |  | VA | Data value | 0.01 | Signed | 5C34 | 1 | 2 | 2
Maximum apparent power L1 |  | VA | Data value | 0.01 | Signed | 5C36 | 1 | 2 | 2
Maximum apparent power L2 |  | VA | Data value | 0.01 | Signed | 5C38 | 1 | 2 | 2
Maximum apparent power L3 |  | VA | Data value | 0.01 | Signed | 5C3A | 1 | 2 | 2
Voltage THD harmonics | THD TENSIONE | % | L1 (THD) | 0.1 | Unsigned | 5D00 | 1 | 1 | 1
|  |  | L1 (2nd,3rd…40th) | 0.1 | Unsigned | 5D01 | 39 | 1 | 39
|  | % | L2 (THD) | 0.1 | Unsigned | 5D80 | 1 | 1 | 1
|  |  | L2 (2nd,3rd…40th) | 0.1 | Unsigned | 5D81 | 39 | 1 | 39
|  | % | L3 (THD) | 0.1 | Unsigned | 5E00 | 1 | 1 | 1
|  |  | L3 (2nd,3rd…40th) | 0.1 | Unsigned | 5E01 | 39 | 1 | 39
|  | % | L1-L2 (THD) | 0.1 | Unsigned | 5E80 | 1 | 1 | 1
|  |  | L1-L2 (2nd,3rd…40th) | 0.1 | Unsigned | 5E81 | 39 | 1 | 39
|  | % | L3-L2 (THD) | 0.1 | Unsigned | 5F00 | 1 | 1 | 1
|  |  | L3-L2 (2nd,3rd…40th) | 0.1 | Unsigned | 5F01 | 39 | 1 | 39
|  | % | L1-L3 (THD) | 0.1 | Unsigned | 5F80 | 1 | 1 | 1
|  |  | L1-L3 (2nd,3rd…40th) | 0.1 | Unsigned | 5F81 | 39 | 1 | 39
Current harmonics | THD CORRENTE | % | L1 (THD) | 0.1 | Unsigned | 6000 | 1 | 1 | 1
|  |  | L1 (2nd,3rd…40th) | 0.1 | Unsigned | 6001 | 39 | 1 | 39
|  | % | L2 (THD) | 0.1 | Unsigned | 6080 | 1 | 1 | 1
|  |  | L2 (2nd,3rd…40th) | 0.1 | Unsigned | 6081 | 39 | 1 | 39
|  | % | L3 (THD) | 0.1 | Unsigned | 6100 | 1 | 1 | 1
|  |  | L3 (2nd,3rd…40th) | 0.1 | Unsigned | 6101 | 39 | 1 | 39
|  | % | N (THD) | 0.1 | Unsigned | 6180 | 1 | 1 | 1
|  |  | N (2nd,3rd…40th) | 0.1 | Unsigned | 6181 | 39 | 1 | 39
Unbalances | SBILANCI | % | Line voltage | 0.1 | Unsigned | 6200 | 1 | 2 | 2
|  | % | Phase voltage | 0.1 | Unsigned | 6202 | 1 | 2 | 2
|  | % | Current | 0.1 | Unsigned | 6204 | 1 | 2 | 2